CBPMII System Power Supply Controls:
There are three types of power supply controls installed in the tunnel. They are controlled via the CESR control system. What follows is a summary of each type and how to control them.

Individual bpm power supply on/off control (CBPM PWR ALL):
Each bpm location has a bit in the control system which allows for the turning on/off the bpm module power supply. These bits are contained within the CBPM PS CYC RLY array as follows:
LOCATION	ELEMENT	LOCATION	ELEMENT
0E	99	OW
1E	98	1W	1
2E	97	2W	2
3E	96	3W	3
4E	95	4W	4
5E	94	5W	5
6E	93	6W	6
7E	92	7W	7
8E	91	8W	8
9E	90	9W	9
10E	89	10W	10
11	88	11W	11
12E	87	12W4	12
13E	86	13W	13
14E	85	14W	14
15E	84	15W	15
16E	83	16W	16
17E	82	17W	17
18E	81	18W	18
19E	80	19W	19
20E	79	20W	20
21E	78	21W	21
22E	77	22W	22
23E	76	23W	23
24E	75	24W	24
25E	74	25W	25
26E	73	26W	26
27E	72	27W	27
28E	71	28W	28
29E	70	29W	29
30E	69	30W	30
31E	68	31W	31
32E	67	32W	32
33E	66	33W	33
34E	65	34W	34
35E	64	35W	35
36E	63	36W	36
37E	62	37W	37
38E	61	38W	38
39E	60	39W	39
40E	59	40W	40
41E	58	41W	41
42E	57	42W	42
43E	56	43W	43
44E	55	44W	44
45E	54	45W	45
46E	53	46W	46
47E	52	47W	47
48E	51	48W	48
49E	50

47AE	112	47AW	108
43AE	113	43AW	107
14E2	117	12W3	104
		12W2	103
		8AW	101

Sector bpm power supply on/off control (CBPM PS RLY):
Each sector of the tunnel has a bulk power supply which distributes power to the individual bpm modules. Each sector power supply has a bit in the control system which allows for the turning on/off of the supply. These bits are contained in the CBPM PS RLY as follows:
CBPM PS RLY 1	0W to 12W3
CBPM PS RLY 2	13W to 25W
CPBM PS RLY 3	26W to 38W
CBPM PS RLY 4	39W to 48W
CBPM PS RLY 5	39E to 49E
CBPM PS RLY 6	26E to 38E
CBPM PS RLY 7	13E to 25E
CBPM PS RLY 8	0E to 12E
Setting any of these elements to a ‘1’ will turn the power supply ON. Setting a ‘0’ to any of these elements will turn the power supply OFF.

Sector Ethernet switch/moxa power supply on/off control (ETH RACK PS):
Each sector of the tunnel has a rack which contains an ethernet switch and MOXA which serve the bpm modules in that sector. Each rack has a bit in the control system which allows for the turning on/off of the power to the switch and MOXA. These bits are contained in the ETH RACK PS as follows:
ETH RACK PS 1	0E to 12E
ETH RACK PS 2	13E to 25E
ETH RACK PS 3	26E to 38E
ETH RACK PS 5	39E to 39W
ETH RACK PS 11	26W to 38W
ETH RACK PS 12	13W to 25W
ETH RACK PS 13	0W to 12W3
Setting any of these elements to a ‘1’ will turn the power supply ON. Setting a ‘0’ to any of these elements will turn the power supply OFF.

Command Reference:
fff vxputn cbpm ps rly 1 1 0	(turn off)
fff vxputn cbpm ps rly 1 1 1	(turn on)