## Sheet1
resolved | # | Issue / Task | Brought up by | Judged/ resolved by | Amount of efforts needed | Relevant for the prototype | priority if any | Comment
yes | 1 | Static heat load of 5% of full design heat load means valve control a problem with low flow. Need exchangeable plug and seats in 2 K supply valve | Reviewer | Dan | little | no |  | Agreed. The Weka valves are designed for this. Max reduction is 5-10% nominal flow. See Dans file
almost | 2 | HOM cooling with 40 – 80 K flow may result in unbalanced flows with unequal heat loads. We suggest planning tests of unbalanced loads on thermal intercept circuits. One could also consider adding some flow resistance on the 40 K side of the capillary cooling tube to the HOM absorbers. | Reviewer | Eric | medium | yes | medium | to be tested at ICM? Calculations indicate it might not be an issue. Maybe on has to test it separately. (see file from Eric). The pipe used there is standard (2.1 mm ID)
| 3 | merged with item 2 | Reviewer | Eric
yes, has to be designed | 4 | In a large ERL system, one could add a bypass valve (from 4.5 K supply to 6 K return) at turnaround at far end for 4.5 to 6 K flow control. | Reviewer | Dan | little | no |  | Probably not, we will use the 4.5K to HGRP bypass for 4.5K supply line cool-down
yes, has to be designed | 5 | In a large ERL system, consider adding a bypass valve at cryoplant end from 40 K manifold to 80 K return. | Reviewer | Dan | little | no |  | Yes, we should put at either the cryo plant end or the far end – whichever is easier. This bypass will allow for keeping the shield cold and provide extra flow for the cryo plant if necessary. End section has do be designed lateron
Yes | 6 | We suggest no active pumping while cold. May not need temperature sensors on 2-ph line except for cool-down and warm-up. Measure helium gas return pipe pressure at feed box. | Reviewer | Peter | little |  | high | Valve for pumping, temp.sensor on the prototype and pressure gauge at feed box
| 7 | Pressure vessel requirements may be more relaxed than for a DOE lab but still require some attention (generally meet intent of the codes). | Reviewer | James | medium | yes | high
yes, as far as the prototype is concerned | 8 | It is an interesting analytical result that pump-down may provide a slight asymmetric deformation of the vacuum vessel resulting in lateral motion of the cavity by 0.3 mm. | Reviewer | Yun | medium | yes |  | By changing boundary conditions the banana deformation vanished. Might be reconsidered towards final ERL design
yes | 9 | For the large ERL string cool-down, a bypass line from the 5 K line to the 300 mm pipe could provide some extra cool-down flow to the pipe to alleviate the different cool-down rates of the cavities and 300 mm pipe. | Reviewer | Dan | little | no |  | Yes, locate at far end. See task 22
yes | 10 | Piping will be a bit different in the prototype cryomodule relative to a production ERL cryomodule, but no big axial loads. (Bellows at reduced pipe ends are different.) 80 K to 120 K cooling of HOM absorbers, not 40 K to 80 K. Valves will be in the production cryomodule positions and environment | Reviewer | Dan | medium | yes | medium | This is just a remark
yes | 11 | The ERL cryomodule interconnect bellows should have internal sleeves | Reviewer | Dan | little | no |  | The 2” bellows will have an internal liner similar to above. The HGRP should also have a bellows liner. SS-liners are commercial, Ti has to be checked
| 12 | Pipes in the ERL cryomodule interconnect will have to be checked for stability against lateral offset with pressure. The sheet metal thermal shield may not be sufficiently rigid support | Reviewer | Yun | medium | yes | high | first ideas are presented, needs more discussion
yes, to be designed | 13 | Axial loads should be taken by end boxes in the ERL system | Reviewer | Yun | medium | partially |  | Expected force: 2 tons. End sections have to be designed accordingly
| 14 | Prototype cryomodule provides a different situation not requiring reaction of large loads. But attention still needs to be given to thermal contraction and pipe support and stability. | Reviewer | Yun | medium | yes | medium | more discussion needed
| 15 | Cryovalves cannot afford displacements (1mm is OK), additional flexibility to be considered | Reviewer | Dan | medium | yes | high | flexing the pipes seems to be easy but an additional support of the valve cold part seems to be necessary
| 16 | If 1.6K to be considered as a fall back solution, specific checks of corresponding circuit to be made (valves, LHe pipe, GHe pipe) | Reviewer | Eric | medium |  | low
yes | 17 | With factor 2 margin w.r.t. 2K heat loads considered for possible bad Q of 2 cavities, operating scenario for static losses of 5% of installed capacity to be envisaged for early days (could be done with smaller valve plug at stem extremity) | Reviewer | Dan | little |  |  | same as task 1!
partially | 18 | Balance of flow in parallel circuits within a cryo-module 40K loop: How to accommodate with a defective HOM 40K warmer than the others (even with 1 heater per loop)? | Reviewer | Eric | medium | no | medium | connected to task 2
| 19 | Balance of flow in parallel circuits within a cryo-module 5K loop: What are the provisions to compensate or effects (and the single heater – inlet- would not help) | Reviewer | Eric | little | yes | medium | Try to calculate things using HePak database
| 20 | Balanced flows: additional instrumentation and/or valves on the prototype would help and allow to quantify it | Reviewer | Eric | little | yes | medium
Yes | 21 | One additional valve at linac extremity to guarantee minimal flow in thermal shield manifold while operating at reduced capacity | Reviewer | Dan | little | no | low | same as task 5!
yes, to be designed | 22 | For cool-down, a by-pass valve at extremity of the linac between 5K and 2K supply lines (both low pressure rating) would help cooling the Helium Gas Return Pipe | Reviewer | Dan | little | no |  | will be foreseen. Caution has to be taken in order not to presurize cavities and HGRP. See also task 9
| 23 | Prototype extremities to be looked at in more details for thermal contraction compensation, pressure effect on supply interface and relative movements between pipes | Reviewer | Yun | medium | yes | low
yes | 24 | Operation of HOM in the prototype will be at higher temperature, inducing extra load on the 5K intercept that should be explicitly evaluated to avoid detrimental effects on the Niobium 1.8K part (sc transition?) | Reviewer | Ralf | medium | yes | high | The heat via conduction will be intercepted at 5K, the radiation het will increas less than 18 mW to 2K which will not be a problem
| 25 | Baffle for low pressure gas looks by far an elegant alternative to 2nd connection as it would effectively cool the HGRP extremity while keeping the 2K-2phase pipe standard | Reviewer | Joe | medium | yes | medium
| 26 | The overall 1.5 safety factor should be split into specific contingencies for all components and temperatures and continuesly updated as design evolves | Reviewer | Eric | medium |  | low
| 27 | The ERL team should make every use of intermediate tests and prototypes to reduce the uncertainty in the various dynamic heat load terms. | Reviewer | Ralf | medium | yes | medium
yes | 28 | Cold electrical feed throughs should be avoided. Room temperature feed throughs should be used instead | Reviewer | Peter | medium | yes | high | Yes, Helium level stick design will be similar to the ICM
yes | 29 | No active vacuum pumping while cold but having provision of one pump port per module | Reviewer | Ralf | little | yes | high | one 5+" port on top forseen, connected to task 6
yes | 30 | Having 2 room temperature pressure transducers on the the He Gas return pipe (one on each end of the linac) should be sufficient | Reviewer | Peter | little | no |  | Has to go into the endsection design
yes | 31 | The additional of a small reservoir on the two phase tube at the end of each cryomodule to allow more accurate level measurement should be considered | Reviewer | Joe | medium | yes | high | no. Reservoir might not be a good representative for the level due to the small manifold pipe
yes | 32 | Should the coupler be straight at 300 K or at 2 K? | Matthias | Matthias | little | yes |  | Reviewers commented that it would be fine ether way. Decission was made to have the couplers at 300 K
| 33 | Buckling of the high pressure lines | Matthias | Dan | medium | yes | high | covered by task 12?
yes | 34 | Stress relieve of the HGRP required | Matthias | Tim | little | yes |  | to be specified in the purchase order, TIO found a vendor for that
| 35 | Develop a beam off scenario with reduced (20 bar) pressure | Matthias | Eric | medium | no | low
yes | 36 | Having BPMs in the middle of beamline string? | Yun | Ralf | medium | yes | medium | Will have antennas in one HOM load flush with the beam pipe similar to the HTC
for now, yes | 37 | Replace the brass bushing with roller bearings for side posts; if so, some modifications are needed for the top flange of vac vessel; | Yun | Yun |  | yes |  | bushing will stay, later change to roller bearings might be considered again
yes | 38 | Survey arrangement with regard to fiducials on the vac vessel – Joe has started to talk with Jim Sexton on this; | Yun | Joe | medium | yes | high | agreement has been achieved
yes | 39 | Details of the magnetic shielding | Ralf | James | medium | yes |  | Cryperm around He vessel, Mumetal around thermal shield (80K), no degausing of the vac vessel
| 40 | Gatevalve support still open | Ralf | Joe | medium | yes | medium | under design, not related to the vac vessel design
| 41 | Finalizing HOM Design: 2/3 bellow convolutions, alignment and mounting procedure, heater position, OVERALL LENGTH | Ralf | Ralf | medium | yes | high | Overall length seems to be fine, choice of material is open
yes | 42 | Decision on 3D CAD model: cold or warm reference | Ralf | Tim | medium | yes | high | Will be a warm reference. We required cold measures will be added
| 43 | Check design status on WPM | Ralf | Joe |  | yes | high | open
Yes | 44 | Gate valve cryogenic heat load calculation/ optimization, replaceing part with G10? | James | Joe | medium | yes | medium | heat load would be 6 W with G10 compared to 16 W without. Probably is not worth the effort (compared to 1200 W coming from the HOMs)
yes | 45 | inter module beam vacuum pump port to be replaced by pumping port on gate valve? | James | Ralf | little | no | low | yes, if we buy new gate valves
| 46 | Beam vacuum rupture disk/ releave port, possibly at the gate valve position | James | Ralf | medium | no | medium | yes, but has to be defined!
| 47 | check position of the gate valve drive | James | Joe | little | yes | high
yes | 48 | No of MLI Layers to be decided (5 between 80 K and 4 K)? | James | Yun | little | yes | medium | 30 layer at 80K, 20 at 2K
yes | 49 | CF Flanges on the cavity HE Vessel (cool-down/ warmup) to be replaced by welds? | James | Dan | little | yes | medium | no. Flanges transition will remain as it makes also the SS to Ti transition
yes | 50 | HEX-Can to MLC connection to be welded | James | Dan | little | yes | medium | flanges should be fine as we expect several reassemblies
| 51 | Define the pressure ratings | Ralf | Ralf | medium | yes | high | Vacuum Vessel to stay below .5 bar
| 52 | Carefull risc assesment | Ralf | Yun | medium | yes | high
| 53 | Insulation vaccum pumping through the MLI and the thermal shield | Ralf | Yun | medium | yes | medium

## Sheet2
select one
Ignore
Low
Medium
High